## Electrical
DOE BUILDING GUIDELINES 2020 CODE COMPLIANCE CHECKLIST
| ENERGY EFFICIENCY |  | Developer |  | Regulator
Item | Requirements | Applicability | Required value | Design Value | Design Compliance
[5 empty] | Documentation needed | Document Provided? | Design Specification Relevant
Electrical Systems (Lighting) | [5 empty] | Yes/No | Yes/No | Remarks
7.1 | Daylighting, Photoelectric Switch and/or Automatic Dimmer |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
| All regularly occupied spaces inside the building shall employ features that can allow daylight into the room space. These can be any or a combination of the other features or daylighting provisions: | Applies to all regularly occupied spaces of all building occupancies except building spaces where daylight access hinders intended functions |  |  | Floor Plan or Roof Plan – showing daylighting provisions and the intended use of the spaces
1 | Windows |  | Window openings shall at least be 10% of the room space floor area |  | Calculations to show that window openings equivalent to at least 10% of the floor space have been provided for all regularly occupied spaces
2 | Light Shelf |  |  |  | Building Elevations and Sections – showing daylighting provisions such as windows, light monitors, clerestory, scoops, light shelves, atrium, skylights, etc.
3 | Clerestory |  |  |  | Daylight Provisions Details – detailed drawings of daylighting provisions |  |  |  | 3770
4 | Skylight |  |  |  | Technical data of the glass - showing the SHGC value |  |  |  | 3880
5 | Light monitor/light scoop |  |  |  | Reflected Ceiling Plan – showing the location of lights, photosensors and/or occupancy sensors |  |  |  | 4080
6 | Other devices that can allow daylight inside |  |  |  | Interior Lighting Design Floor Plan – showing the layout of the fixed/permanent lighting fixtures, circuitry and control (i.e., toggle switches, sensor switches, programmable timer, etc.) and technical specifications of the lighting system.
Lighting Control Diagram – showing the control logic of the various sensors and controllers employed
| Where adequate day lighting is available, local manual or automatic controls such as photoelectric switches or automatic dimmers shall be provided in the day-lit spaces. Controls shall be provided so as to operate rows of lights parallel to the facade/exterior wall. If occupancy sensors are installed in the daylight zone, the occupancy sensor shall override the photoelectric sensor during non-occupancy periods. | For residential condominiums, this applies only to common indoor areas with access to daylight. |  |  | Technical Data Sheets (TDS) of the various sensors and controllers employed |  |  |  | 11730
| The light fixtures equipped with photoelectric sensor shall be located approximately at half (½) the depth of the daylight zone. | Installed lighting fixtures within the day-lit zones are exempt from using photoelectric sensor if this hinders its intended functions. | The photoelectric sensor shall be located approximately at half (½) the depth of the daylight zone. |  | Justification for the non-usage of photosensors due to the fact that it hinders the intended function of the lighting fixture
7.2 | Integrated Lighting and Air Conditioning Luminaires |  | Required Value | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
| For buildings with centralized air conditioning equipment, consideration shall be given to integrated lighting and air conditioning systems which use luminaires with heat removal capabilities. | Applies to buildings with centralized air conditioning system using integrated lighting and air conditioning luminaires. |  |  | Air conditioning and ventilation system ceiling plan with section drawings
Integrated lighting and air conditioning luminaire detail drawings
3 | Efficient Lighting System Selection |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | The lighting system shall be designed for expected activity. The designer shall select the most efficient lamps, the proper color rendition and the desired color appearance appropriate for the type of lighting needed for the space to be lit. The most efficient combination of luminaires, lamps, and ballasts appropriate for the lighting task and for the environment shall be selected so that lamp light output is used effectively. The selected luminaire shall meet the requirements with respect to light distribution, uniformity, and glare control. | Applies to all building occupancies without exceptions | Required |  | Interior Lighting Design Floor Plan
Exterior Lighting Design Drawings
Lighting product technical brochure
4 | Emergency Lighting |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Buildings with at least ten (10) storeys shall have at least one LED lamp in each corridor, emergency exit, and stairwell per storey. Each elevator shall also have at least one LED lamp (with light output of at least 500 lumens), which shall always be lit and designed to have a separate circuit from the usual lighting circuit, which is not controllable by a switch, and is supplied by the UPS System of the building. | Applies to buildings with at least ten (10) storeys. |  |  | Reflected Ceiling Plan
Interior Lighting Design Floor Plan
Exterior Lighting Design Drawings
UPS design circuitry drawings, calculations and technical specifications
5 | Finishing |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Light finishes shall be employed to attain the best overall efficiency of the entire lighting system. Dark surfaces shall be avoided because these absorb light. | Applies to all building occupancies without exceptions | Required |  | Interior Finishing Design Floor Plan
Interior Design Floor Plan
6 | Lighting Control |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Each enclosed space or room shall be provided with at least one control point (e.g., switch) for lighting. Likewise, one lighting control point shall be provided for each task lighting. However, for enclosed areas 10 m2 or larger, the lighting design and/or control device shall be able to reduce lighting by at least 50%, while maintaining a reasonably uniform level of illuminance throughout the area, through the use of dimmers, dual switching of alternate lamps or by switching each luminaire or each lamp. When dimming control of lighting will be needed, rheostat-based dimmers shall not be used; only electronic dimmers are allowed. | Applies to all regularly occupied spaces of all building occupancies except building spaces where continuous lighting is required for emergency/security purposes. | Required |  | Architectural Reflected Ceiling Plan
Electrical lighting and switching circuitry layout
Lighting control diagram
Technical Specifications
7 | Lighting Power Density (LPD) |  | LPD Calculator | Design Value | Documentation needed | Document Provided? | Design Specification Relevant
a | Building LPD within maximum LPD requirements | Applies to all building occupancies without exceptions | W/m2 | W/m2 | Architectural Reflected Ceiling Plan w/ LEGEND Box
a.1 | Residential Dwelling |  | 10.8 | 0 | Electrical Lighting Layout w/ LEGEND Box
a.2 | Hotel/Resort |  | 10.8 | 0 | Building Lighting Power Density Table
a.3 | Educational: School |  | 12.9 | 0 | Technical specifications of light fixtures
a.4 | Institutional: Hospital |  | 12.9 | 0
a.5 | Business: Office |  | 10.8 | 0
a.6 | Mercantile:Mall (excluding accent lighting) |  | 16.1 | 0
a.7 | Exterior facade |  | 2.15 | 0
a.8 | Active entrance (pedestrian conveyance) |  | 98.4 | 0
a.9 | Inactive entrance (normally locked/inactive) |  | 65.6 | 0
a.10 | Covered Parking |  | 3.2 | 0
a.11 | Open Parking |  | 1.6 | 0
8 | Occupancy Sensors |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Occupancy sensors linked to lighting shall be installed in areas with variable occupancy. | Applies to all building occupancies except for hospitals and malls and for emergency and security lighting | Required |  | Architectural Reflected Ceiling Plan
b | Occupancy sensors in covered parking lighting system - at least 60% of lighting |  | Required |  | Electrical Lighting layout
Interior Lighting Design Floor Plan
Exterior Lighting Design Drawings
Occupancy Sensing System Confirmation Table
Technical Data Sheets (TDS) of the various sensors and controllers employed
9 | Exterior Lighting |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Exterior lighting not intended for 24 hours continuous use shall be automatically switched off, when not needed through the use of timer, photocell, or a timer-photocell combination but provided with manual override. | Applies to all building occupancies without exceptions | Required |  | Exterior Lighting Design Drawings
Technical Data Sheets (TDS) of the various sensors and controllers employed
10 | Lighting Control Location |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | All lighting controls shall be installed near the point of entry of a particular space and shall be readily accessible to space occupants. Switches for task lighting areas may be mounted as part of the task lighting fixtures. Switches controlling the same load from more than one location shall not be credited as increasing the number of controls to meet the requirements of Table 41 of Guidelines on Energy Conserving Design of Buildings. | Applies to all building occupancies except for lighting control requirements for spaces, which shall be used as a whole, shall be controlled in accordance with the work activities and controls may be centralized in remote locations. | Required |  | Interior Lighting Design Floor Plan
For hotels and motels, guest rooms’ electrical power and lighting circuitry showing the key activated master switch or other similar control device
11 | Hotel/Motel Guest Rooms |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Every guest room of hotels and motels shall be equipped with a master switch, which shall be located by the main entry door and may be activated by the insertion (instantaneous) and removal (either instantaneous or with a short time delay) of the room key or any other similar control device that automatically switches on or off the master switch after detecting occupancy or non-occupancy of a room, respectively. | Applies to such building occupancies except when continuous lighting is required for emergency/security purposes. | Required |  | Interior Lighting Design Floor Plan
Technical Data Sheets (TDS) of the various sensors and controllers employed
12 | Display and Valance Lighting |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | For retail and wholesale stores, feature display and valance lightings shall have separately switched circuits. Each feature display lighting circuit shall be designed to have total calculated load of not more than 20 amperes. If there are more than four of these feature displays circuits, the display lighting shall be automatically controlled by a programmable timer with provisions for temporary override by store personnel. | Applies to building occupancies with retail and wholesale stores. | Required |  | Interior Lighting Design Floor Plan
Exterior Lighting Design Drawings
Electrical Systems (Motors)
13 | Minimum Efficiency Performance Requirements for Motors |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | The performance of a motor shall equal or exceed the nominal full load efficiency levels given in Table 42 of the DOE Building Guidelines | Applies to all building occupancies except for submersible motors, motors that are integrated into a systems and motors designed to operate at extremely high or low temperatures, in explosive environments (ATEX), or at altitudes above 1000 meters above sea level. | Required |  | Motor Schedule
Technical Data Sheets and/or brochures of the motors
14 | Motor Sizing |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | The type and the size of the squirrel-cage induction motor shall be selected only after an accurate determination of the starting and running requirements of the load has been made. | Applies to all building occupancies without exceptions | Required |  | Technical Data Sheets and/or brochures of the motors
15 | Variable Speed/Frequency Drive Provision and Total Harmonic Distortion |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | All blower, fans and pumps requiring speed control operation shall use variable speed/frequency drives. | Applies to all building occupancies except for kitchen ventilation fans and non-centralized air conditioning systems. | Required |  | Floor Plan
Motor Schedule
Technical Data Sheets and/or brochures of the all VSD/VFD/s and Soft Starter/s.
16 | Energy Performance Requirements for Cooling Systems |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | For cooling systems using motors, either the Energy Efficiency Factor (EEF) or the Cooling Seasonal Performance Factor (CSPF) shall be the measure of energy performance that shall apply. | Applies to all building occupancies without exceptions | Required |  | Floor Plan
Technical Data Sheets and/or brochures of the all VSD/VFD/s and Soft Starter/s.
17 | Soft Starters |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Soft starters with energy optimization shall be used in starting all simple constant speed operation application of motors. | Applies to all building occupancies without exceptions | Required |  | Floor Plan
Technical Data Sheets and/or brochures of the all VSD/VFD/s and Soft Starter/s.
18 | Pumps |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | A pump shall be properly sized for its application to attain a flow near peak efficiency maintaining a flow between 80% and 100% of the Best Efficiency Point (BEP). | Applies to all building occupancies without exceptions | Required |  | Floor Plan
Technical Data Sheets and/or brochures of the all VSD/VFD/s and Soft Starter/s.
19 | Overhead Water Tank/s |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | All buildings with at least ten (10) storeys shall be provided with overhead or elevated water tank/s with a total capacity of 120% of the calculated average daily water demand of the building. | Applies to buildings with at least ten (10) storeys. |  |  | Roof Plan
Water Line Single Line or Schematic Diagram
Water tank detailed drawings and technical specifications
20 | Escalators and Moving Ramps/Walkways Operations and Motor Drive |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Escalators and moving ramps/walkways shall reduce speed when no traffic is detected for a maximum period of one and a half (1-1/2) minutes and stop or go on standby mode after five (5) minutes of no activity. | Applies to all building occupancies without exceptions | Required |  | Floor Plan
Building Section Drawings
Technical Data Sheets and/or brochures of the all VSD/VFD/s and Soft Starter/s.
Technical Data Sheets and/or brochures of the motors
Mechanical Equipment Schedule
Process control diagrams of escalators, moving ramps/walkways and elevators
21 | Elevator Motor Drives |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | All buildings that are required to have elevators shall be designed to have elevators run by motors coupled to a Variable Voltage and Variable Frequency (VVVF) drive. | Applies to all building occupancies except for hydraulic elevators and buildings without elevators. | Required |  | Floor Plan
Technical Data Sheets and/or brochures of the all VSD/VFD/s and Soft Starter/s.
Technical Data Sheets and/or brochures of the motors
22 | High-Capacity Escalator and Elevatora |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | For airports, train stations, high-rise (i.e., 10 storeys or higher) buildings and the like, with high-capacity escalators and elevators that travels long downward distances, its escalators and elevators shall have motors equipped with VSDs/VFDs coupled with line regenerative drives. | Applies to such building occupancies except for low-capacity escalators and escalators with short downward travel distances. | Required |  | Floor Plan
Building Section Drawings
Technical Data Sheets and/or brochures of the all VSD/VFD/s and Soft Starter/s.
Technical Data Sheets and/or brochures of the motors
23 | Elevator Lighting |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Elevator car, including display and emergency, lighting shall use lamps with efficacies, across all fittings in the car, of at least 80 lumens/watt. | Applies to all building occupancies without exceptions | Required |  | Lighting Plan of the Elevator Car
24 | Elevator Operations |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | The elevator/s shall operate in a standby mode and all lighting of the elevator car, except the emergency lighting, shall switch off when no activity has been detected for a maximum period of five (5) minutes; said duration may be adjusted, depending on the demand. | Applies to all building occupancies without exceptions | Required |  | Mechanical Equipment Schedule
Process control diagrams of escalators, moving ramps/walkways and elevators
Electrical Systems (Electric Power Distribution)
25 | Transformers |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | All transformers that are to be part of the building’s electrical system shall have efficiencies not lower than 98%. | Applies to all building occupancies without exceptions | Required |  | Technical data sheet or brochure of the transformer/s
b | The high (voltage) side of the main transformer of the building shall be connected in delta, while the low (voltage) side shall be connected in wye, with its neutral is available for grounding.
26 | Power Factor |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | The average power factor of all the loads being served by the transformers at any time shall not be less than what is required in the latest edition of the Philippine Distribution Code (PDC). | Applies to all building occupancies without exceptions | Required |  | Power factor computation
Power factor correction computation and assumptions
CHCI computation
Technical data sheet or brochure of the power factor correction device/equipment, all motors and lighting loads.
27 | Transformer Loading |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Transformer load grouping schemes shall be so designed such that the main transformer/s is loaded to not less than 60% of its full load ratings, and that no-load circuits or partially loaded circuit combinations shall be minimized as much as possible. | Applies to all building occupancies without exceptions | Required |  | Technical data sheet or brochure of the transformer/s
Main transformer capacity calculation and assumptions
28 | Circuit Breakers and Disconnect Switches |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | In compliance with the Philippine Distribution Code, disconnect switch/es and circuit breaker/s shall be provided at the primary (supply) side of the transformer to allow electrical disconnection during no load period. | Applies to all building occupancies without exceptions | Required |  | Single line diagram of the service entrance and high voltage side of the main transformer/s
Technical data sheets or brochures of the main circuit breaker and disconnect switches
29 | Transformer Vault/Room |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Transformers located inside a building shall have sufficient ventilation and have direct access from the road for ease of maintenance at all times. The ambient temperature within the transformer vault/room shall be controlled in such a way that it will not exceed 30oC. | Applies to all building occupancies except when the main transformer is not enclosed in a vault/room. | Required |  | Detailed Floor Plan and Layout.
30 | Wire/Cable Sizes | Applies to all building occupancies without exceptions | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | In the calculation of the wire sizes to be used, the designer shall follow the procedure specified in the latest edition of the Philippine Electrical Code (PEC), Part I, considering the factors stated therein so as to arrive at the minimum acceptable wire size. |  | Required |  | Architectural Reflected Ceiling Plan
Electrical lighting and switching circuitry layout
Lighting control diagram
Technical Specifications
31 | THD and TDD |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | The design Total Harmonic Distortion (THD) and Total Demand Distortion (TDD) for a three-phase circuit at the connection point of the building to the distribution system shall not exceed the limits specified in the Philippine Distribution Code (PDC), which is 5%. | Applies to all building occupancies without exceptions | Required |  | Architectural Reflected Ceiling Plan w/ LEGEND Box
Supplier’s technical data sheets and/or brochures of the electronic ballasts, self-ballasted lamps (CFL and LED), VSDs/VFDs, UPS, inverter appliances, DC drives
32 | Maximum Current Unbalance |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | For three-phase, four-wire circuits with single-phase loads, the maximum current unbalance (unbalance single-phase loads distribution) shall not cause the voltage unbalance at the distribution system to exceed the limits specified in the Philippine Distribution Code, which is 2.5%. | Applies to all building occupancies without exceptions | Required |  | Detailed load schedule per phase of the main distribution circuit
Design drawings, calculations, technical specifications and technical data sheets and/or brochures of the lightning protection system and surge suppression/protection system
33 | Lightning and Transient Voltage Surge Protection |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | All buildings shall install systems to protect their facilities from the effects of lightning and transient voltage surges, which complies with the relevant provisions in the latest edition of the PEC Part 1. | Applies to all building occupancies without exceptions |  |  | Design drawings, calculations, technical specifications and technical data sheets and/or brochures of the lightning protection system and surge suppression/protection system
34 | Electrical and Similar Room/s Environmental Requirements |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Electrical vaults/rooms, switchgear rooms, generator rooms, in-door substations, control rooms, relay rooms, battery rooms, metering rooms, SCADA and Telecommunications rooms, and other similar rooms, shall have sufficient natural or mechanical ventilation to keep the room temperatures below 30oC and the relative humidity at the range of 75-95% non-condensing. | Applies to all building occupancies without exceptions |  |  | Detailed Floor Plan and Layout
35 | Electric Vehicle (EV) Parking with Charging Stations |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Private and public buildings and establishments covered by these guidelines and pursuant to Republic Act No. 6541, otherwise known as the National Building Code of the Philippines, shall designate dedicated parking slots for the exclusive use of Electric Vehicles (EVs). The number of dedicated parking slots shall be proportional to the total number of parking slots within the building or establishment as mandated by said law. | Applies to all building occupancies without exceptions |  |  | Detailed Plan and Layout of the EV Parking/Charging Spaces
b | Further, all designated EV parking areas shall be provided with charging stations or electric vehicle supply equipment (EVSE) for use in charging the EVs.
36 | Uninterruptible Power Supply (UPS) System |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | All buildings with at least ten (10) storeys shall have a UPS System with enough capacity to power the emergency/security lighting load of all the corridors, emergency exits, stairwells, elevators, parking spaces, and perimeter areas of a building for at least one (1) hour (back-up time). | Applies to all building occupancies without exceptions |  |  | Detailed plan of the UPS supplied circuits, particularly for emergency lighting, capacity calculations, technical specifications and technical data sheets and/or brochures of the UPS [9.12];
37 | Emergency/Standby Generator Set |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Buildings with elevators are required to have emergency generator sets with the adequate standby power ratings/capacities to supply power to, at least, the elevators and the various emergency and safety systems of the building for a limited duration (i.e., enough time to evacuate persons trapped inside the elevators) during commercial power outages. | Applies to all building occupancies without exceptions |  |  | Technical data sheets and/or brochures of the emergency generator set/s, automatic transfer switch
b | Further, an automatic transfer switch (ATS) shall be installed to transfer the power source from the usual local power utility to the emergency/back-up power source, after a short delay, during commercial power interruptions.
c | The generator set’s fuel consumption at 100% rated capacity shall not go over 0.28 liters per kWh.
38 | Power Metering |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Covered buildings shall have metering facilities capable of measuring voltage, current, power factor, power quality, maximum demand and energy consumption. | Applies to all building occupancies without exceptions |  |  | Electrical Power Single Line Diagram
Technical data sheets and/or brochures
39 | Building Management System |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Buildings are encouraged to install Building Management Systems (BMS), with analytics and optimization software, to have centralized monitoring and control of the many individual systems within the building. | Applies to all building occupancies without exceptions |  |  | Technical data sheets and/or brochures
Electrical Power Distribution Layout
Technical Specifications
40 | Smart Home System |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Residential dwelling buildings, such as condominiums, are encouraged to employ smart home technologies in every home unit, which shall be equipped with sensors, devices and appliances that are connected to the Internet of Things (IoT) and are able to be remotely monitored, controlled and accessed by the home owner. | Applies to all building occupancies without exceptions |  |  | Electrical Power Single Line Diagram
41 | Inspection and Thermal Scanning | Applies to all building occupancies without exceptions | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | During the testing and commissioning phase of the various building systems, inspection and thermal scanning shall be conducted on all transformers, panel boards, conductors and connectors to check for hot spots. |  |  |  | Technical data sheets and/or brochures
42 | Regular Inspection, Maintenance, Monitoring and Energy Audit | Applies to all building occupancies without exceptions | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Buildings shall conduct annual inspection and maintenance of its electrical systems, such as thermal scanning of the transformers, panel boards and conductors to check for hot spots, which are sources of losses in a distribution system and, at the same time, possible causes of electrical fires. Buildings, at the onset of operation, shall monitor and record their monthly energy consumption in order to establish a baseline value. Covered buildings shall conduct regular energy audit of its facilities. |  |  |  | Electrical Power Single Line Diagram
Electrical Power Distribution Layout
Technical Specifications
Electrical Systems (RE Systems)
43 | RE Power Supply System |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Buildings shall install RE power supply systems within their facility, whenever it is technically feasible, either at their rooftops, façades, grounds and/or roofed parking spaces. | Applies to all building occupancies without exceptions |  |  | Detailed Roof, Facade and/or Grounds Plan and Layout
Single line diagram/s showing the building’s internal distribution system
Detailed design of the RE power supply system
Technical data sheets and/or brochures of the various RE equipment
44 | RE Power Supply System Capacity |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | RE power supply system capacity can be sized to either supply partially the energy requirements of the facility (own use), or supply entirely the energy requirements of the facility (Net Zero Energy Building) or, aside from satisfying its own power requirements, sell the excess energy to the local power utility (Net Metering, which, presently, is up to 100 kW only but may be raised by ERC in the future). | Applies to all building occupancies without exceptions |  |  | Single line diagram/s showing the building’s internal distribution system
Detailed design of the RE power supply system
Technical data sheets and/or brochures of the various RE equipment
45 | RE Power Supply System Design |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | RE power supply system shall be designed and installed in accordance with the relevant provisions of the latest editions of the Philippine Electrical Code Part 1, the Philippine Distribution Code, applicable rules and regulations issued by ERC and the Office of the Building Official and by the rules and interconnection procedures established by the local distribution utility under which franchise the building is covered. | Applies to all building occupancies without exceptions |  |  | Single line diagram/s showing the building’s internal distribution system
Detailed design of the RE power supply system
Technical data sheets and/or brochures of the various RE equipment
46 | RE Power Supply System Metering |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | RE power supply systems shall be equipped with at least two (2) meters; one measuring, among others, the quantity of RE power being supplied to the building, and the other measuring the quantity of commercial power (i.e., from the local electric utility) being supplied to the building. | Applies to all building occupancies without exceptions |  |  | Single line diagram/s showing the building’s internal distribution system
Detailed design of the RE power supply system
Technical data sheets and/or brochures of the various RE equipment
47 | Annual Energy |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Covered buildings shall source, initially, a minimum of one percent (1%) of their projected annual energy requirements (subject to adjustments by DOE from time to time) from RE sources. | Applies to all building occupancies without exceptions |  |  | Detailed Roof, Facade and/or Grounds Plan and Layout
| 1. RE Power Supply Systems |  |  |  | Detailed design of the solar LED street lights (if applicable)
| 2. Solar Water Heaters |  |  |  | Technical data sheets and/or brochures of the solar PV panels, inverter/s, solar cables, combiner boxes and metering
| 3. Solar Cooling Systems |  |  |  | Technical data sheets and/or brochures of the various RE equipment
| 4. Solar-Powered Lighting Systems |  |  |  | Detailed Floor and/or Roof Plan and Layout
5. Any other similar system or equipment
6. Green Energy Option Program (GEOP)
| DECLARED BY | Signature |  |  | Signature
(Name of Design Professional)
DECLARED BY
(Name of In-charge of Construction)
| VERIFIED BY | Signature |  |  | Signature
(Name of LGU OBO Checker)

## LPD Calculator
LIGHTING POWER DENSITY CALCULATOR
| Uses | Total Units |  | Designed Total Lighting Power (Watts) | Designed Total LPD
| Residential | 0 | m2 | 0 | 0 | W/m2
| Hotel | 0 | m2 | 0 | 0 | W/m2
| School | 0 | m2 | 0 | 0 | W/m2
| Hospital | 0 | m2 | 0 | 0 | W/m2
| Office | 0 | m2 | 0 | 0 | W/m2 |  |  | A27A58A2A5
| Mercantile/Retail | 0 | m2 | 0 | 0 | W/m2
| Covered Parking | 0 | m2 | 0 | 0 | W/m2
| Open and Outdoor Parking | 0 | m2 | 0 | 0 | W/m2
| Exterior Façade | 0 | m2 | 0 | 0 | W/m2
| Active Entrance | 0 | m | 0 | 0 | W/m
| Inactive Entrance | 0 | m | 0 | 0 | W/m
Return to Electrical GB Checklist
Building Space | Uses | Unit |  | Designed Total Lighting Power | Designed LPD |  | GB Code Required | Not Complied
Delete Unused Rows |  |  |  | (Watts) |  |  |  | 100
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied
|  | 0 |  | 0 | 0 |  |  | Not Complied

## Sheet1
Required | Complied | YesNo | Provided | Use | LPD | Units
Required | Complied | Yes | Provided | Residential | 10.8 | W/m2 | m2
Not Required | Not Complied | No | Not Provided | Hotel | 10.8 | W/m2 | m2
Exempt | Not Applicable |  |  | School | 12.9 | W/m2 | m2
|  |  |  | Hospital | 12.9 | W/m2 | m2
|  |  |  | Office | 10.8 | W/m2 | m2
|  |  |  | Mercantile/Retail | 16.1 | W/m2 | m2
|  |  |  | Covered Parking | 3.2 | W/m2 | m2
|  |  |  | Open and Outdoor Parking | 1.6 | W/m2 | m2
|  |  |  | Exterior Façade | 2.15 | W/m2 | m2
|  |  |  | Active Entrance | 98.4 | W/m | m
|  |  |  | Inactive entrance | 65.6 | W/m | m