## Mechanical
DOE BUILDING GUIDELINES 2020 COMPLIANCE CHECKLIST
| ENERGY EFFICIENCY |  | Developer |  | Regulator
Item | Requirements | Applicability | Required value | Design Value | Design Compliance
[5 empty] | Documentation needed | Document Provided? | Design Specification Relevant
Mechanical Systems (Air Conditioning and Ventilating Systems) | [5 empty] | Yes/No | Yes/No | Remarks
1 | Load Calculation |  | Required? | Complied? | Documentation needed | Document Provided | Design Specification Relevant
a | Cooling system design loads for the purpose of sizing the system and equipment shall be determined in accordance with the procedures in the latest edition of the ASHRAE Handbook of Fundamentals or other equivalent publications. The indoor conditions in an air-conditioned space shall conform with the design conditions set in the Guidelines on Energy Conserving Design of Buildings | Applies to all building occupancies with centralized air-conditioning system | Required |  | Load Calculation
2 | System Design |  | Required? | Complied? | Documentation needed | Document Provided | Design Specification Relevant
a | Air conditioning system and equipment shall be sized as close as possible to the space and system loads calculated in accordance with the subsection on load calculation. Engineered system and equipment shall be properly sized and selected to meet maximum loads and shall have good unloading characteristics to meet the minimum load efficiency.Considerations shall be given at the design stage for providing centralized monitoring and control to achieve optimum operations with minimum energy consumption | Applies to all building occupancies with centralized air-conditioning system | Required |  | System design and sizing
3 | Fan Systems |  | Required? | Complied? | Documentation needed | Document Provided | Design Specification Relevant
a | For fan systems that provide a constant air volume whenever the fans are operating, the power required by the motor of the combined fan system at design conditions shall not exceed 0.5 W/m3/h. | Applies to all building occupancies with centralized air-conditioning system | Required |  | Mechanical Drawings
b | For fan systems that are able to vary system air volume automatically as a function of load, the power required by the motor of the combined fan system at design conditions shall not exceed 0.5 W/m3/h. Individual VAV fans with motor rated at 5 kW and larger shall include control and devices such as a variable speed drive necessary to make the fan motor operate efficiently even at flow rates of as low as 40% of the rated flow. Electronically commutated (EC) motors shall be used |  | Required |  | Equipment Schedule
Technical Specifications
4 | Pumping System |  | Required? | Complied? | Documentation needed | Document Provided | Design Specification Relevant
a | Chilled water and cooling water circuits of air conditioning systems shall be designed at a maximum velocity of 1.2 m/s (3.9 fps) for a 50 mm diameter pipe and pressure drop limit of 39.2 kPa per 100 (4 ft/100 ft) equivalent meter for piping over 50 mm diameter. | Applies to all building occupancies except for (1) System where a minimum ow greater than 50% of the design ow rate is required for the proper operation of the equipment served by the system, (2) Systems that serve only one control valve, or (3) System with total pump motor requirement of 5 kW or less. | Required |  | Mechanical Drawings
b | Pumping systems that are provided with control valves designed to modulate or step open or close, depending on the load, shall be required for variable fluid flow. The system shall be capable of reducing system flow to 50% of design flow or less. |  | Required |  | Equipment Schedule
Technical Specifications
5 | Air Distribution Systems |  | Required? | Complied? | Documentation needed | Document Provided | Design Specification Relevant
a | The temperature and humidity of the air within the conditioned space shall be maintained at an air movement from 0.20 to 0.30 m/s (39 fpm to 59 fpm). | Applies to all building occupancies with centralized air-conditioning system | Required |  | Mechanical Drawings
Equipment Schedule
Technical Specifications
6 | Controls | Applies to all building occupancies | Required? | Complied? | Documentation needed | Document Provided | Design Specification Relevant
a | Each air-conditioned system shall be provided with at least one control device for temperature regulation. |  | Required |  | Mechanical Drawings
b | All mechanical ventilating system (supply and exhaust) equipment, either continuously operating or not, shall be provided with readily accessible manual and/or automatic controls or other means of volume reduction, or shut-off when ventilation is not required. |  | Required |  | Equipment Schedule
Technical Specifications
7 | Chiller Plant Insulation |  | Required? | Complied? | Documentation needed | Document Provided | Design Specification Relevant
a | All chilled water piping shall be thermally insulated in accordance with Table 20 to prevent heat gain and avoid sweating on the insulation surface. | Applies to all building occupancies with centralized air-conditioning system | Required |  | Equipment Schedule
Piping & Instrumentation Diagrams
8 | Air Handling System Insulation |  | Required? | Complied? | Documentation needed | Document Provided | Design Specification Relevant
a | All air handling ducts and plenums installed as part of the air distribution system and which are outside of air-conditioned spaces shall be thermally insulated sufficiently to minimize temperature rise of the air stream within them, and to prevent surface condensation. | Applies to all building occupancies except (1) when the heat gain of the ducts, without insulations, shall not increase the energy requirements of the building or (2) for exhaust air ducts | Required |  | Equipment Schedule
b | Insulated ducts located outside of buildings shall be jacketed for rain tightness and for protection against damage. |  | Required |  | Piping & Instrumentation Diagrams
c | Air ducts or plenums within air-conditioned spaces may not be insulated if the temperature difference (TD) between the air outside and within the ducts or plenum would not cause surface condensation. Due consideration shall be made to the dew point temperature of the air surrounding the ducts or plenums.
9 | Air Conditioning Equipment |  | EER or COP or kW/Ton | EER or COP or kW/Ton | Documentation needed | Document Provided | Design Specification Relevant
a | Air conditioning equipment shall have a minimum performance corresponding to the rated conditions shown in Table 21 of the Building Guidelines | Applies to all building occupancies | Required |  | Mechanical Drawings
b | The performance rating of the air conditioning equipment above 14 kW (3.95 TR) shall be measured by its EER or kWe/TR, whichever is applicable. The EER shall not be less than those quoted in Table 22, while kWe/TR shall not be greater than the figures in the same table |  | Required |  | Equipment Schedule
Technical Specifications
10 | Heat Recovery Systems |  | Required? | Complied? | Documentation needed | Document Provided | Design Specification Relevant
a | All buildings with a centralized air supply system shall use an enthalpy recovery wheel or energy recovery ventilation with the efficiency of at least 60% of 90% of exhaust air. When buildings have outside air or fresh air supply and they extract air through mechanical means, heat exchangers can use the air extracted from the building area to pre- condition the incoming outdoor air. This process takes into account the fact that the extracted air is usually already conditioned, and therefore colder and drier. | Applies to all building occupancies with centralized air-conditioning system | Required |  | Equipment Schedule
Mechanical Equipment layout and schematic diagram
Technical Specifications of Enthalpy Recovery Wheel
11 | Natural Ventilation and Lighting |  | Required? | Complied? | Documentation needed | Document Provided | Design Specification Relevant
a | In natural regulations, it is specified that every building shall have: (a) natural lighting through windows, skylights, fanlights, doors, and other approved natural light-transmitting media; and (b) natural ventilation through windows, skylights, fanlights, doors, louvers, or similar ventilation openings. | Applies to all building occupancies. | Required |  | Detailed floor plans
b | In general, openings facing the sky, street courtyard, or air well shall be considered as acceptable sources of natural lighting and ventilation. |  | Required
c | In the case of a building other than a factory or warehouse, any part of the building within 9 m from an acceptable opening is considered adequately ventilated by natural means. |  | Required
d | In the case of a factory or warehouse, the maximum effective coverage of any window and other openings on an external wall is 12 m from the opening, whereas the coverage of any jack roof or other openings on the roof is 9 m, measured horizontally from the opening. |  | Required
e | In addition, every room in any building shall have natural lighting and ventilation through one or more sources having an aggregate of not less than x percent of the oor space of the room, of which at least y percent shall have an opening to allow free uninterrupted passage of air. The respective values of x and y are given in Table 23 according to the types of occupancy or types of usage of the room. |  | Required
f | In the case of public garages, two or more sides of the garage shall have an opening for cross ventilation and the area opening will be at least 50% of the area of the wall where it is located. |  | Required
10 | Germicidal Irrardiation Systems |  | Required? | Complied? | Documentation needed | Document Provided | Design Specification Relevant
a | A germicidal irradiation filtration system is needed for air handling units (AHUs) and fan coil units (FCUs) for efficient disinfection. | Applies to all building occupancies with centralized air-conditioning system | Required |  | Equipment Schedule
Air-conditioning & Ventilation Layout
Technical Specifications of the various AC equipment
11 | Car Park Ventilation Systems |  | Required? | Complied? | Documentation needed | Document Provided | Design Specification Relevant
a | Enclosed parking garage ventilation systems shall automatically detect contaminant levels by using supervisory control and data acquisition (SCADA) or building management systems (BMS). | Applies to all building occupancies with enclosed parking garage. | Required |  | Detailed Floor Plan
Ventilation Layout
Technical Specifications of the various equipment
Mechanical Systems (Steam and Hot Water Systems)
12 | Steam and Water System Design and Sizing | Applies to all building occupancies except building with no water heating system and buildings using solar water heating and/or heat pump for water | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | A. The system with the lowest overall energy usage (considering the heat losses in the calorifier and the circulating loop of a centralized system and the total heat losses from a system of individual storage heater) shall be chosen. |  | Required |  | Load Calculation
b | Steam is more economical compared with electricity. Where steam is available, use steam to generate hot water. |  | Required |  | System design and sizing
c | When steam is used, a centralized hot water generator shall be placed as near as possible to the steam source to reduce piping heat losses. |  | Required
13 | Water Heating System |  | Required Efficiency Factor | Efficiency Factor | Documentation needed | Document Provided? | Design Specification Relevant
a | All boilers and hot water storage tanks shall meet the criteria in Tables 29, 30, 31 of the Guidelines on Energy Conserving Design of Buildings 2020 | Applies to all building occupancies except building with no water heating system and buildings using solar water heating and/or heat pump for water |  |  | Equipment Schedule
| (Equipment 1) |  |  |  | Plumbing & Electrical power layout
| (Equipment 2) |  |  |  | Technical Specifications of Water Heating system
(Equipment 3)
(Equipment 4)
(Equipment 5)
14 | Steam and Water System Controls |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Hot water systems shall be equipped with effective automatic temperature controls | Applies to all building occupancies except building with no water heating system and buildings using solar water heating and/or heat pump for water | Required |  | Equipment Schedule
b | Systems designed to maintain usage temperatures in the circulating loop shall be equipped with automatic time switches or other controls that can be set to turn off the system when use of hot water is not required |  | Required |  | Piping & Instrumentation Diagrams
15 | Steam and Water System Insulation |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | The insulation of steam, condensate, and hot water lines shall conform to the requirements in Table 30 the Guidelines on Energy Conserving Design of Buildings 2020. | Applies to all building occupancies except those without centralized cooling systems | Required |  | Equipment Schedule
Piping & Instrumentation Diagrams
16 | Waste Heat Recovery |  | Required? | Complied? | Documentation needed | Document Provided? | Design Specification Relevant
a | Recover waste heat from the chilled water system for water heating | Applies to all building occupancies except those without centralized cooling systems | Required |  | Mechanical Equipment Layout and Schematic Diagram
b | Storage shall be used to optimize heat recovery when the flow of heat to be recovered is out of phase with the demand for hot water. |  | Required |  | Technical Specifications
| DECLARED BY | Signature |  |  | Signature
(Name of Design Professional)
DECLARED BY
(Name of In-charge of Construction)
| VERIFIED BY | Signature |  |  | Signature
(Name of LGU OBO Checker)

## Load Estimation
Air Conditioning Cooling Load Estimate
Project |  |  | By
Location |  |  | Date
Length (ft) |  | x Width (ft) |  | = Floor Area (sq.ft.)
Heigth (ft)
By-pass Air Factor (BF) | 0.15
Conditions | Dry Bulb, F | Wet Bulb, F | %RH | Graid/lb
Outdoor
Room
Difference
Ventilation
| cfm/person |  | x persons | = |  | cfm
| cfm/sq.ft. |  | x sq.ft. | = |  | cfm
| TOTAL |  |  |  |  | cfm
| Item | Area |  | Sun Gain/Temp Diff. | U Factor | BTU/Hr
Length, ft.
Height, ft.
Solar Heat Gain
N | Glass |  | x |  | SF x |  | x |  | =
S | Glass |  | x |  | SF x |  | x |  | =
W | Glass |  | x |  | SF x |  | x |  | =
E | Glass |  | x |  | SF x |  | x |  | =
N | Wall |  | x |  | SF x |  | x |  | =
S | Wall |  | x |  | SF x |  | x |  | =
W | Wall |  | x |  | SF x |  | x |  | =
E | Wall |  | x |  | SF x |  | x |  | =
| Roof |  | x |  | SF x |  | x |  | =
Conduction Heat Gain
All Glass |  |  |  |  | x |  | x |  | =
All Wall |  |  |  |  | x |  | x |  | =
Partition |  |  |  |  | x |  | x |  | =
Ceiling |  |  |  |  | x |  | x |  | =
Floor |  |  |  |  | x |  | x |  | =
Roof |  |  |  |  | x |  | x |  | =
Internal Heat Gain
Occupants | [5 empty] | persons | x | 245 | =
Light |  | watts |  | number |  | =total watts | x | 3.42 | =
Power | [5 empty] | HP | x | 2546 | =
[6 empty] | kW | x | 3415 | =
[6 empty] | Room Sensible Heat |  |  | =
Ventilation
1.08 | x |  | x | 20 | x | 0.15 | x | cfm | =
[6 empty] | Effective Room Sensible Heat |  |  | =
Latent Heat Gain
Occupants |  | persons | x | 205 |  |  |  |  | =
Ventilation
| cfm |  | gr/lib |  | BF | x | 0.68 |  | =
[6 empty] | Effective Room Latent Heat |  |  | =
[6 empty] | Effective Room Total Heat |  |  | =
Outside Air
Outside Air Sensible |  | cfm |  | F | 1.08 | x | 0.15 | x BF | =
Outside Air Latent |  | cfm |  | gr/lib | 0.68 | x | 0.15 | x BF | =
[6 empty] | Total Outside Air |  |  | =
[5 empty] | GRAND TOTAL HEAT in BTU/hr |  |  |  | =
[5 empty] | in Tons of Refrigeration |  |  |  | =
Psychrometery
ESHF | = | ERSH |  | =
ERTH
Indicated ADP |  | F | Selected ADP |  | F
Temp. Rise | = (1 - 0.15 BF) x (75 deg F - selected ADP)
Dehum Air | = | ERSH |  |  | = |  | CFM
1.08 x Temp Rise

## Min Ventilation Rate Calculator
MINIMUM VENTILATION RATE CALCULATOR
Room Parameters (Delete Unused Rows) |  |  |  | 2010 PSVARE Standard |  | Required |  |  | Equipment |  | Not Complied
Space | Room/Space Designation | Floor Area (m2) | Space Occupancy (Person) | Area Outdoor Airflow Rate (CMH/m2) | People Outdoor Airflow Rate (CMH/person) | Designed Area Outdoor Air Flow (CMH/m2) | Designed People Outdoor Air Flow (CMH/m2) | Designed Total Air Flow (CMH/m2) | Schedule Designation | Air Flow (CMH/m2) | 100
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Not Complied
Return to Mechanical GB Checklist

## Sheet1
Required | Complied | YesNo | Provided | Equipment Type | Minimum Efficiency
Required | Complied | Yes | Provided | Through-the-wall, air-cooled, split systems <31,655 KJ/H | 12.0 SEER
Not Required | Not Complied | No | Not Provided | Through-the-wall, air-cooled, single packaged <31,655 KJ/H | 12.0 SEER
Exempt | Not Applicable |  |  | Small-duct high velocity, air cooled <68,585 KJ/H | 10.0 SEER
|  |  |  | Air-cooled, split systems <68,585 KJ/H | 12.0 EER
|  |  |  | Air-cooled, single packaged <68,585 KJ/H | 11.6 EER
|  |  |  | Air cooled ≥68,585 KJ/H | 11.5 EER
|  |  |  | Air cooled <142,447 KJ/H | 11.3 EER
|  |  |  | Air cooled ≥142,447 KJ/H | 11.5 EER
|  |  |  | Air cooled <253,238 KJ/H | 11.3 EER
|  |  |  | Air cooled ≥253,238 KJ/H | 10.0 EER
|  |  |  | Air cooled <801,922 KJ/H | 9.8 EER
|  |  |  | Air cooled ≥801,922 KJ/H | 9.5 EER
|  |  |  | Water cooled <68,585 KJ/H | 14.0 EER
|  |  |  | Water cooled ≥68,585 KJ/H | 13.8 EER
|  |  |  | Air cooled chillers with condenser, electrically operated | 10.0 EER
|  |  |  | Water cooled, Electrically operated, positive displacement <75 tons | 0.78 Kw/ton
|  |  |  | Water cooled, Electrically operated, positive displacement ≥75 tons | 0.775 Kw/ton
|  |  |  | Water cooled, Electrically operated, positive displacement ≥150 tons | 0.68 Kw/ton
|  |  |  | Water cooled, Electrically operated, positive displacement ≥300 tons | 0.62 Kw/ton
|  |  |  | Water cooled, Electrically operated, centrifugal <300 tons | 0.634 Kw/ton
|  |  |  | Water cooled, Electrically operated, centrifugal ≥300 tons | 0.576 Kw/ton
|  |  |  | Water cooled, Electrically operated, centrifugal ≥600 tons | 0.57 Kw/ton
|  |  |  | Air-cooled and Water cooled absorption single effect | 0.6 COP
|  |  |  | Absorption double effect indirect-fired | 1.0 COP